# Checklist for Infection Control

## Concerns when reopening healthcare facilities closed due to extensive water and wind damage

Prior to opening a healthcare facility that has undergone extensive water and wind damage, inspections need to be conducted to determine if the building is salvageable. If the decision is made to proceed with recovery and remediation, building and life safety inspections must be completed before any restoration work is done to the facility. Parts I–IV describe those activities that need to be completed. Parts V–VII provide guidance for infection control review of facilities to be performed before the hospital can reopen.

Prior to opening any portion of a facility such as emergency rooms or clinics, adequate support services need to be available to provide quality care in a safe environment. Contracting with outside services could be considered.

Certification for occupancy must be obtained prior to reopening the facility. Regulations regarding healthcare facility certification and licensing differ from state to state. Refer to specific state and local government resources for more information.

1. Safety Evaluation

The following should be evaluated by facilities experts:

Structural integrity and missing structural items

Assessment of hidden moisture

Electrical system damage, including high voltage, insulation, and power integrity

Water distribution system damage

Sewer system damage

Fire emergency systems damage

Air handling system damage

Medical waste and sharps disposal system

2. Water Removal

Water should be removed as soon as possible once the safety of the structure has been verified.

Pump out standing water

Wet vacuum residual wetness from floors, carpets, and hard surfaces

Clean wet vacuums after use and allow to dry

3. Water Damage Assessment and Mold Remediation

Open the windows in the damaged areas of the building during remediation

Remove porous items that have been submerged or have visible mold growth or damage

Minimize dispersion of mold spores by covering the removed items and materials with plastic sheeting (dust-tight chutes leading to dumpsters outside the building may be helpful). Dispose these items as construction waste

Seal off the ventilation ducts to and from the remediation area and isolate the work area from occupied spaces, if the building is partially occupied

Scrub and clean hard surfaces with detergents to remove evidence of mold growth (if a biocide is used, follow manufacturer’s instructions for use and ventilate the area. Do not mix chlorine-containing biocides with detergents or biocides containing ammonia)

Dry the area and remaining items and surfaces

Evaluate the success of drying and look for residual moisture in structural materials (Moisture-detection devices [e.g., moisture meters] or borescopes could be used in this evaluation.)

Remove and replace structural materials if they cannot be dried out within 48 hours

4. Inspect, Repair, Disinfect where Appropriate, or Replace Facility Infrastructure. Include:

HVAC system (motors, duct work, filters, insulation)

Water system (cold and hot water, sewer drainage, steam delivery, chillers, boilers)

Steam sources (if piped in from other places, e.g., utility companies, it will impact autoclaves)

Electrical system (wiring, lighting, paging and patient call systems, emergency generators, fire alarms)

Electronic communication systems (telephones, paging and resident call systems, computers)

Medical gas system

Hazardous chemicals/radioactive storage

5. General Inventory of Areas with Water and Wind Damage

What furniture can be salvaged? Discard wet porous furniture that cannot be dried and disinfected (including particle board furniture). Disinfect furniture with non-porous surfaces and salvage. Discard upholstered furniture, drapery, and mattresses if they have been under water or have mold growth or odor. Discard all items with questionable integrity or mold damage

What supplies can be salvaged? Salvage linens and curtains following adequate laundering. Salvage pre-packaged supplies in paper wraps that are not damaged or exposed to water or extreme moisture, or in a molded environment. Discard items if there is any question about integrity or mold exposure. Dry essential paper files and records (professional conservators may be contacted for assistance)

Electrical medical equipment. Check motors, wiring, and insulation for damage. Inspect equipment for moisture damage. Clean and disinfect equipment following manufacturer’s instructions. Do not connect wet electronic equipment to electricity

Structures. Inspect, repair, or replace wallboard, ceiling tiles, and flooring. Repair, replace, and clean damaged structures

6. Review Issues for Reopening Facilities

Requirements needed prior to opening a facility: potable water, adequate sewage disposal, adequate waste and medical waste management

Have all areas to be opened been thoroughly dried out, repaired, and cleaned?

Does the number of air exchanges in areas of the facility meet recommended standards?

Are negative-pressure rooms functioning properly?

8. Post-Reoccupation Surveillance

Focused microbial sampling may be indicated to determine if:

- The water in the facility’s water distribution system meets the microbial standards of the Safe Drinking Water Act (see: http://www.epa.gov/safewater/sdwa/index.html);

- Mold remediation efforts were effective in reducing microbial contamination in the affected areas of the hospital (see: http://www.epa.gov/mold/mold_remediation.html);

- Residents who are receiving care in the reopened facility acquire infections that are potentially healthcare associated and that may be attributed to Aspergillus spp. or other fungi, non-tubercular mycobacteria, Legionella, or other waterborne microorganisms above expected levels